##### VIRGINIA DEPARTMENT OF TRANSPORTATION

##### LOCATION AND DESIGN DIVISION

###### DRAINAGE DESIGN MEMORANDUM

| GENERAL SUBJECT: #### MANAGEMENT OF STORMWATER | NUMBER: #### DDM 2 |
| --- | --- |
| SPECIFIC SUBJECT: Engineering and Plan Preparation | DATE: # November 17, 1999 |
|  | SUPERSEDES: #### LD-99 (D) 195.3 |

BACKGROUND

- Acts of the General Assembly have resulted in the issuance of Stormwater Management (SWM) and Erosion and Sediment Control (E&S) regulations.  The general application to highway operations associated with these regulations is addressed in this memorandum.  Instructions for the incorporation of the E&S details in plan assemblies are contained in the current version of I&IM LD-(D) 11.

- Additional details and examples of the engineering application of the State SWM regulations in the design of VDOT projects can be obtained from the VDOT Hydraulics Section in any of the various district offices or the central office in Richmond.

- Further details and information regarding either the State SWM Regulations or the E&S Regulations can be obtained from: Virginia Department of Conservation and Recreation (DCR), 203 Governor Street, Richmond, VA 23219 or via the Internet: www.state.va.us/~dcr. Details may also be obtained from the SWM Handbook and the E&S Handbook published by DCR and available for reference in all VDOT Hydraulics Sections.

OBJECTIVE

SWM

- To inhibit the deterioration of the aquatic environment by instituting a stormwater management program that maintains both water quantity and quality post development runoff characteristics, as nearly as practicable, equal to or better than pre-development runoff characteristics.

E&S

- To effectively control soil erosion, sediment deposition, and post development runoff to minimize soil erosion and to prevent any sediment from escaping the project limits.

CRITERIA

General

- The runoff control provisions of both regulations are complementary and will be addressed under a single set of criteria.  The information and instructions contained in this memorandum supersede all previous departmental documents.  Where there are conflicts with previous instructions, this memorandum shall take precedence.

- The Erosion and Sediment Control Regulations apply to all activities that disturb 929 square meters (10,000 square feet) or more of land area.

- The Stormwater Management Regulations are applicable to all state projects.

EXEMPTIONS

- Linear development (highway) projects are exempt from the STORMWATER MANAGEMENT REGULATIONS provided that:

- Less than one acre of new impervious area will be added per outfall and

- There will be insignificant increase in peak flow rates and

- There are no existing or anticipated flooding or erosion problems downstream.

- “State Projects” are those land development activities wherein VDOT has funded any portion of the design, right of way acquisition, or construction (including public/private partnerships used for constructing state highways).  Projects which are designed and constructed by other parties and that are accepted into the state system for maintenance after completion of construction (including subdivision streets) are not considered state projects and must conform to appropriate local regulations.  Land development activities occurring within existing VDOT right of way, which are allowed by permit and which are designed, constructed, and funded by other parties, are not considered state projects and must conform to appropriate local regulations.

- “Land Development Project” is defined as a manmade change to the land surface that potentially changes its runoff characteristics as a permanent condition.  The permanent condition should consider the effects of mature vegetative cover and should not be concerned with temporary changes due to construction activities.  The temporary changes are addressed by the E & S regulations.

Water Quantity Control

- Water quantity control shall be governed by the Virginia Erosion and Sediment Control Regulations Minimum Standard 19 which requires an adequate receiving channel for stormwater outflows from all projects with more than 929 square meters (10,000 square feet) of land disturbance.

- Receiving channels, pipes and storm sewers shall be reviewed for adequacy based upon the following criteria:

Natural channels shall be analyzed by the use of a 2-year storm to verify that stormwater will not overtop channel banks or cause erosion of the channel bed and banks.  All previously constructed manmade channels shall be  analyzed by the use of a 10-year frequency storm to verify that the stormwater will not overtop the banks and analyzed by the use of a 2-year storm to verify that the stormwater will not cause erosion of the bed or banks.  Pipes and storm sewer systems shall be analyzed by the use of a 10-year frequency storm to verify that the stormwater will be contained within the pipe or storm sewer system.  The receiving channel at the outlet of the pipe or storm sewer shall be analyzed for adequacy of the 2-year storm for natural channels or the 10-year storm for man made channels.

- Water quantity control for the 1-year storm (in lieu of the 2 year storm required by Minimum Standard 19) may be needed if there is existing or anticipated erosion downstream.  Control of the 1-year storm requires detaining the volume of runoff from the entire drainage area and releasing that volume over a 24-hour period.  The computations are similar to those used for detaining the

- Water Quality Volume (WQV) and releasing over a 30-hour period.  See the SWM Handbook by DCR: pages 1-23 and 5-38 thru 5-41.  When the 1-year storm is detained for 24 hours there will be no need to provide additional or separate storage for the WQV if it can be demonstrated that the WQV will be detained for approximately 24 hours.  The control of the 1-year storm may require a basin size that is 1.5 to 2 times larger than a basin used to control the increase in Q from a 2-year or a 10-year storm.

- Pre-development conditions shall be that which exist at the time the road plans are approved for right of way acquisition.  All land cover shall be assumed to be in good condition regardless of actual conditions existing at the time the computations are made.

- Impounding structures (dams) that are not covered by the Virginia Dam Safety Regulations shall be checked for structural integrity and floodplain impacts for the 100-year storm event.

- Outflows from the stormwater management facilities shall be discharged into an adequate receiving channel.

- Existing swales being utilized as natural outfall conveyances for pre-development run-off will be considered as channels and, if the swale satisfactorily meets the criteria contained in Minimum Standard 19 of the Virginia Erosion and Sediment Control Regulations for post-development run-off, it will be considered as an adequate receiving channel.

- Surface runoff from drainage areas of three acres or more that pass through a disturbed area must be controlled by a sediment basin.  The sediment basin shall be designed and constructed to accommodate the anticipated sediment loading from the land disturbing activity and adjacent property within the watershed that has a high erosion potential.  The design of the outfall device or system shall take into account the total drainage area flowing through the basin.

- Construction of stormwater management facilities should be avoided in floodplains.  When this is unavoidable, a special examination to determine the adequacy of the proposed stormwater management facilities during the 10-year flood shall be required.  The purpose of this analysis is to ensure that the stormwater management facility will operate effectively.  The stormwater management facility shall also be examined for structural stability during the passage of the 100-year flood event on the floodplain and shall be examined for any possible impacts caused by the basin on the 100-year flood characteristics of the floodplain.  The construction of stormwater management facilities shall be in compliance with all applicable regulations under the National Flood Insurance Program.

- If it can be demonstrated that the total drainage area to the point of analysis within the receiving channel is 100 times greater than the contributing drainage area of the project,

the receiving channel may be considered adequate, with respect to channel stability requirements under the Erosion & Sediment Regulations, without further computation.

Water Quality Control

- SWM design for water quality control is to be in accordance with the latest revisions to the Virginia SWM Regulations.  The following comments represent the significant points of the current regulations and the page numbers given are referenced to the SWM Handbook from DCR.

- BMP requirements for quality control are “Technology Based” and the type of BMP is determined by the percent of new impervious area within the site (or Right of Way) per outfall (SEE TABLE 1 – BMP SELECTION TABLE) and also the drainage area size (in accordance with the general design criteria as outlined in the SWM Handbook).

- BMP requirements for flooding or quantity control are set by the Erosion and Sediment Control Regulations Minimum Standard 19 for adequate receiving channels.

- Extended Detention Basins and Extended Detention Basins Enhanced require a Water Quality Volume (WQV) of 2 x the standard WQV or 1” of Runoff from the new impervious area.

- Extended Detention Basins and Extended Detention Basins Enhanced require a 30-hour drawdown time for the required WQV.  The 3” minimum size water quality orifice has been eliminated.  If the required orifice size is found to be significantly less than 3” an alternative water quality BMP should be investigated such as a linear facility which treats the first flush and allows large storms to overflow.  The calculation procedure for drawdown time and orifice sizing is shown on PAGES 5-33 THRU 5-38 and also in example problems available from VDOT.

- Sediment Forebays should be used on Extended Detention Basins and Extended Detention Basins Enhanced with the volume set as 0.1” – 0.25” x the new impervious area or 10% of the required detention volume.  SEE DETAILS PAGE 3.04-6.  The stabilized overflow spillway may be constructed of riprap or concrete.

- Suggested details for the Extended Detention Basin are shown on PAGES 3.07-04 AND 3.07-5.  The riprap lined low flow channel thru the basin is not recommended by VDOT due to maintenance concerns.

- Suggested details for the Extended Detention Basin Enhanced are shown on PAGES 3.07-6 AND 3.07-7.  The geometric design will probably need to be more symmetrical than shown in order to construct the basin to the dimensions needed.

- Non-structural practices including, but not limited to, control of land use development, minimization of impervious areas and curbing requirements, open space acquisition, floodplain management, and protection of wetlands may be utilized as appropriate in order to at least partially satisfy the water quality requirements.  Approval of such non-structural measures will be secured in advance from the Department of Conservation and Recreation (DCR).

MULTI-USE BASINS

Quantity Control – Quality Control – Temporary Sediment Storage

SWM basins will normally be used for both quantity control and for quality control.  Under the revised regulations some basins may occasionally only be needed for quality control.  Most SWM basins are needed to serve as temporary sediment basins and the design and computations will need to address the dual function.  The design that is needed for a permanent SWM basin may need to provide additional temporary sediment storage volume that is in excess of the required WQV.  The two different volumes (WQV and temporary sediment storage volume) should not be added together and the larger of the two should govern the design.  The additional volume needed for sediment storage may be provided by excavating the bottom of the basin lower than required for WQV.  The permanent outlet structure (riser or wall) can be temporarily altered to serve as the control structure for the sediment basin.  (See the enclosed design detail drawings and the DCR SWM Handbook).  When the project is nearing completion and the basin is no longer needed for sediment control, the basin can be easily converted to a permanent SWM basin.

IMPLEMENTATION

Plan Preparation

- Standard and minimum plan projects shall show stormwater management and erosion control measures on the plans as directed in IIM LD- (D) 11 and the Road Design Manual.

- No-plan projects must have the erosion and sediment control measures included in the construction narrative addressing their placement.  This narrative may be supplemented by appropriate “simple” sketches.  Stormwater management facilities may be addressed in a similar fashion provided sufficient detail is included to ensure their proper construction.  When this is not practicable, additional sketches shall be included in the no-plan assembly to define the construction of these items.

- Any other type of project activity that does not have a plan, such as some SAAP Projects, shall conform to the no-plan requirements.

- Maintenance activities which disturb more than 929 square meters (10,000 square feet) must have a plan developed by the appropriate personnel that addresses the erosion and sediment control requirements for that activity.  Maintenance activities which involve a

- “Land Development Project” of one acre or more of land must have a stormwater management plan.  The plan shall conform to the requirements for a no-plan project.

- Normal ditch cleaning and pulling of shoulders are not considered land disturbing activities for the purposes of erosion and sediment control if less than 929 square meters (10,000 square feet) of drainage area is disturbed feeding any one pipe or ditch outlet.

Foundation Data

- Foundation data (a soil boring) for the base of the dam should be requested for all Stormwater Management Basins in order to determine if the native material will support the dam and not allow ponded water to seep under the dam.  An additional boring near the center of the basin should also be requested if:

- Excavation from the basin may be used to construct the dam, OR

- Rock may be encountered in the area of excavation, OR

- A high water table is suspected which may alter the performance of the SWM basin.

For large basins, more than one boring for the dam and one boring for the area of the basin may be needed.  The number and locations of the borings are to be determined by the drainage designer.

- The foundation data should be requested by the drainage designer when the request is initiated for culvert foundation data.  See I&IM LD-(D) 121.

Right of Way

- Permanent stormwater management facilities may be placed in fee right of way or in permanent easements.  It is recommended that all permanent stormwater management facilities (dams, ponds, risers, etc.) be placed within fee right of way initially.  Ditches and similar features may initially be placed in permanent easements.  The final decision on right of way versus permanent easement can be made at the field inspection or as a result of the design public hearing.  The Department will generally be amenable to the desires of affected landowners in this matter.  The multiple use of property for stormwater management and such features as utilities is permissible.  The decision on the advisability of such actions must be made on an individual site basis.

#### Table 1*

#### BMP SELECTION TABLE

| #### Water Quality BMP | #### Target Phosphorus Removal Efficiency | #### Percent Impervious #### Cover** |
| --- | --- | --- |
| Vegetated filter strip Grassed swale | 10% 15% | 16-21% |
| Constructed wetlands Extended detention (2xWQ Vol) Retention basin I (3xWQ Vol.) | 30% 35% 40% | 22-37% |
| Bioretention basin Bioretention filter Extended detention-enhanced Retention basin II (4xWQ Vol) Infiltration (1xWQ Vol) | 50% 50% 50% 50% 50% | 38-66% |
| Sand filter Infiltration (2xWQ Vol) Retention basin III (4xWQ Vol with aquatic bench) | 65% 65% 65% | 67-100% |

* Innovative or alternate BMPs not included in this table may be allowed at the discretion of DCR.

** Percent Impervious Cover: New impervious area within the site or Right of Way per outfall.

#### DETAILS FOR DESIGN OF DAMS

VDOT STORMWATER MANAGEMENT BASINS

The following details are to be incorporated into the design of VDOT Stormwater Management (SWM) Basins in order to be in compliance with the State SWM Regulations Revisions of 1998 and the SWM HANDBOOK of the Virginia Department of Conservation and Recreation (DCR).  The revisions are also due to concerns with seepage thru the dam and along the culvert due to the ponding of water in the basins being of longer duration than previous designs that used a minimum 3” water quality orifice.

- Foundation data for the dam is to be secured from the Materials Division in order to determine if the native material will support the dam and not allow ponded water to seep under the dam.

- The foundation material under the dam and the material used for the embankment of the dam should be type A-4 or finer* and/or meet the approval of the Materials Division.  If the native material is not adequate, the foundation of the dam is to be undercut a minimum of 4’ or the recommendation of the Materials Division.  The backfill and embankment material must meet the above soil classification or the design of the dam may  incorporate a trench lined with a membrane (such as bentonite penetrated fabric or an HDPE or LDPE liner) and be approved by the Materials Division.

- The pipe culvert under or thru the dam is to be concrete sewer pipe with rubber gaskets.  Pipe Specifications: 232 (AASHTO M170), Gasket Specification: 212 (ASTM C443)

- A concrete cradle is to be used under the pipe to prevent seepage thru the dam.  The concrete cradle is to extend from the riser or inlet end of the pipe to the outlet of the pipe.  See attached Special Design Drawing No. 2209.

- If the height of the dam is greater than 15’ the design of the dam is to include a Homogenous Embankment with seepage controls or Zoned Embankment or similar design and is to be approved by the Materials Division.

*In accordance with the AASHTO Classification System (M145)

#### DESIGN GUIDELINES

FOR

STORMWATER (SWM) BASINS

The top width (W) of the SWM basin dam should be 3m (10’) minimum to facilitate both construction and maintenance.

The side slopes should be no steeper than 3:1 to permit mowing and cleanout.  The bottom slope of the basin should be no more than 2% or no less than 0.5%.

The depth of the basin to the primary overflow (crest of riser, or orifice or weir) should be no more than 1m (3 ft.) if possible, in order to reduce the hazard potential.  If the depth needs to be more than about 1m (3 ft.) fencing should be considered.

All SWM basins should be reviewed for the needs of fencing, barricades and no trespassing signs in accordance with the VDOT guideline for Fencing of SWM Basins.

The length to width ratio should be about 3:1 (wider at the outlet end).  If the ratio is less than about 2:1, and if there is concern that the velocity of flow through the basin is high, consideration should be given to using baffles within the basin to reduce velocity.  Baffles should be constructed of “pervious” type material such as snow fence rather than earth berms which do not reduce the velocity.

Perimeter Controls

- Fencing of SWM Basins

- Fencing of stormwater management basins is normally not required and should not be used for most basins due to:

- Insignificant Hazard

Ponding of water in the basin should only occur with very heavy storms and be noticeable for a few hours.   The ponded depth will normally be no more than

about 1 meter (3 feet).  Ponds and lakes are almost never fenced, even though they may be located in subdivisions and have deep, permanent ponding.

- Limits Maintenance

Fencing will limit maintenance operations and could deter the frequency of maintenance.  Maintenance operations can damage fencing particularly if equipment becomes stuck.

- Fencing of SWM basins may occasionally be needed and should be used when:

- Basin is deep with ponded depth greater than about 1 meter (3 feet) and/or has steep side slopes with 2 or more side slopes steeper than 3:1;

or

- Basin is in close proximity to schools, playgrounds or similar areas where children may be expected to frequent;

or

- Recommended by the Field Inspection Report, the Resident Engineer or the City/County (where City/County will take over maintenance responsibility.)

- Barricades

- A chain or gate may be needed on some basins to prohibit vehicular access if there is concern with dumping or other undesirable access.

- Signs

- “No Trespassing signs” shall be considered for use on all basins, whether fenced or unfenced and should be recommended as needed on the Field Inspection Report.

Regional Facilities

- There are many cases where it is more feasible to develop one large stormwater management facility to control a watershed area rather than a number of small individual facilities controlling small drainage basins.  The concept of regional stormwater management facilities is endorsed by VDOT provided that certain requirements are met.

- Development and use of regional stormwater management facilities must be a joint undertaking by VDOT and the local governing body.  The site must be part of a master stormwater management plan developed by the local governing body and any agreements related to these facilities must be consummated between VDOT and the local governing body.  VDOT will not enter into an agreement with private individuals or corporations.

- Where the roadway embankment serves as an impounding structure, the right of way line will normally be set at the inlet face of the drainage structure.  The local government will be responsible for the maintenance and liabilities outside of the right of way and VDOT will accept the same responsibilities inside the right of way.

- Hydraulic design of regional management facilities must address any mitigation needed to offset increases in runoff from the roadway.  Stormwater management facilities located upstream of the roadway shall provide sufficient mitigation of peak outflow to compensate for roadway runoff which may bypass the facility.

Maintenance

- Requirements for maintenance of stormwater management facilities, the recommended schedule of inspection and maintenance, and the identification of persons responsible for the maintenance will be addressed by the Maintenance Division.

Future Reconstruction

- If a stormwater management facility is constructed to address the increase in runoff from a current project and, at some time in the future, is displaced to accommodate future construction, a new facility constructed at that time must address increases in runoff due to the future construction and the increases in runoff that were mitigated by the original stormwater management facility.

Reporting

- VDOT is required to submit an annual report to the Department of Conservation and Recreation (DCR) that identifies the location, number and type of stormwater management facilities installed during the preceding year, their storage capacities, the affected water body, and a summary of any water quality monitoring data associated with the facility.  A database has been established on the Hydraulics Section’s telecommunication file system to record this type of data for all projects.  It shall be the responsibility of the district drainage engineer and the hydraulic design engineers in the Central office to ensure that the required information is logged on the database for all stormwater management facilities that are designed for roadway projects.  In order for the database to reflect those facilities constructed during the preceding year, it is recommended that the required information be logged at the time of the first submission of plans to the Construction Division.  The reporting period will be from July 1 to June 30.

PLAN DETAILS

Stormwater Management Drainage Structure Standard SWM-1

- To be used at all applicable locations where a drop inlet type control structure is desired.

Stormwater Management Riser Pipe Standard SWM-RP

- To be used at all applicable locations where an open top manhole type control structure is desired.

- Diameters from 900 mm to 1500 mm in 150 mm increments (36” to 60” in 6” increments).

- Height of structure above outlet pipe invert should be limited to about 1 meter (3 feet) maximum.

Stormwater Management Dam

- To be used at locations where a wall type control structure is desired (includes modifications to standard endwalls).  Normally used for shallow depths of ponding.

- Details to be provided for individual locations.

Details of control structures other than those above shall be submitted to the office of the State Hydraulics Engineer to facilitate future development of standard details.

Stormwater Management Details Standard SWM-DR

- Provide at each location requiring a water quality orifice.  The size opening for the water quality orifice shall be specified for each basin.

Access

- A means of access for inspection and maintenance personnel shall be provided at each SWM facility location.

- A turnaround should be provided on vehicular entrances when needed based upon accessibility and traffic volume.

- Appropriate surface material shall be provided for each vehicular entrance.

Method of Measurement – Basis of Payment

Stormwater Management Drainage Structure (SWM-1):

- Basis of payment to be linear meters (feet) measured from invert of structure to top of concrete cover.

Stormwater Management Riser Pipe:

- Basis of payment to be linear meters (feet) of the size specified measured from invert of structure to the top of the structure.

Stormwater Management Dam:

- Basis of payment to be m3 (cubic yards) of Concrete Class A3 Miscellaneous and kilograms (pounds) of Reinforcing Steel.

Grading:

- Excavation for stormwater management basins will be measured and paid for as m3 (cubic yards) of Stormwater Management Basin Excavation.

- If additional fill material is needed for dams or berms this will be measured and paid for as m3 (cubic yards) of Regular Excavation, Borrow Excavation or Embankment.

- The Grading Diagram is to reflect how the m3 (cubic yards) of Stormwater Management Excavation and m3 (cubic yards) of Embankment or Borrow is to be distributed.

Stormwater Management Summary

- All items related to the construction of stormwater management facilities shall be summarized, by location, in a separate summary located on or near the Drainage Summary (see attached example).

- If Borrow or Embankment is needed, include in roadway totals on Grading Diagram and Summary.

PAY ITEMS

The following pay items are established:

| ###### PAY ITEM |  |  | ###### UNIT |  | ###### ITEM CODE |
| --- | --- | --- | --- | --- | --- |
|  |  |  | #### Metric | #### Imperial |  |
| SWM Basin Excavation SWM Drainage Structure (SWM-1) |  |  | m3 m | Cu. Yds. Lin. Ft. | 27545 27550 |
| SWM Riser Pipe SWM Riser Pipe SWM Riser Pipe SWM Riser Pipe SWM Riser Pipe | 900 mm 1050 mm 1200 mm 1350 mm 1500 mm | (36”) (42”) (48”) (54”) (60”) | m m m m m | Lin. Ft. Lin. Ft. Lin. Ft. Lin. Ft. Lin. Ft. | 27560 27562 27564 27566 27568 |
| SWM Dam: Conc. Cl. A3 Misc. Reinf. Steel |  |  | m3 kg | Cu. Yds. Lbs. | 00525 00540 |

| (METRIC) STORMWATER MANAGEMENT CONTROL SUMMARY | DRY RIP RAP CLASS__ |  |  | Metric Tons |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | STORMWATER MANAGEMENT DAM | REINF. STEEL |  | kg |  |  |
|  |  | CONC. CLASS A-3 MISC. |  | m3 |  |  |
|  | STORMWATER MANAGEMENT RISER PIPE |  | 1500 mm | meters |  |  |
|  |  |  | 1350 mm |  |  |  |
|  |  |  | 1200 mm |  |  |  |
|  |  |  | 1050 mm |  |  |  |
|  |  |  | 900 mm |  |  |  |
|  | STORMWATER MANAGEMENT DRAINAGE STRUCTURE SWM-1 |  |  | meters |  |  |
|  | STORMWATER MANAGEMENT BASIN EXCAVATION |  |  | m3 |  |  |
|  | LOCATION |  |  |  |  | TOTAL |

| (IMPERIAL) STORMWATER MANAGEMENT CONTROL SUMMARY | DRY RIP RAP CLASS__ |  |  | Tons. |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | STORMWATER MANAGEMENT DAM | REINF. STEEL |  | Lbs. |  |  |
|  |  | CONC. CLASS A-3 MISC. |  | C.Y. |  |  |
|  | STORMWATER MANAGEMENT RISER PIPE |  | 60" | Lin. Ft. |  |  |
|  |  |  | 54” |  |  |  |
|  |  |  | 48” |  |  |  |
|  |  |  | 42” |  |  |  |
|  |  |  | 36” |  |  |  |
|  | STORMWATER MANAGEMENT DRAINAGE STRUCTURE SWM-1 |  |  | Lin. Ft. |  |  |
|  | STORMWATER MANAGEMENT BASIN EXCAVATION |  |  | C.Y. |  |  |
|  | LOCATION |  |  |  |  | TOTAL |

SPECIAL PROVISION SECTIONS 302 AND 303

- The current Special Provision/Copied Note for measurement and payment for stormwater management items is accessible through the Internet at http://www.vdot.state.va.us.  The path is “Opportunities Network”, “Construction and Maintenance Contracting Opportunities”, “Resources”, “Road and Bridge Specifications”.  Win Zip is available from this web site to enable viewing of the information.  Questions pertaining to the web site may be addressed to the Construction Division (Ms. Mary Roane) at (804) 786-2124.  Questions concerning the Special Provisions/Copied Notes may be addressed to Ms. Norma Gilbert at (804) 786-2356.  Please note the effective advertisement date for these provisions.