## Electrical Distribution

The procedure used to develop the electrical system for a rest area or parking lot is similar to the discussion in Section V – Roadway Lighting, Appendix VB-4 Electrical Distribution.  However, the electrical system in a parking area normally functions on 120/240-Volt, or 120/208-Volt, single-phase power.  The Amp-Balance and Voltage Drop tables along with the Example Electrical Schematic presented below match the lighting layout shown in the example rest area plans in Appendix VIA-5, Rest Area Lighting Plan Sheet and Appendix VIA-6, Rest Area Lighting Panelboard Schedule.

| Table 1 |  |  |  |  |  |  |  |  |  | PAGE | x | OF |  | y |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| VDOT Project Name |  |  |  |  |  |  |  |  |  | MADE BY: | JH | DATE |  |  |  |  |  | 08/10/00 |  |  |
| LUMINAIRE LAYOUT AND AMP BALANCING |  |  |  |  |  |  |  |  |  | CHKD. BY | TG | DATE |  |  |  |  |  | 01/17/00 |  |  |
| REST AREA CONTROL CENTER |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Circuits 2, 4 (Truck Parking & Ent. Ramp) |  |  |  |  |  |  |  |  |  | Circuits 3, 5 (Car Parking & Pedestrian Lighting) |  |  |  |  |  |  |  |  |  |  |
| LUM | WATT |  | AMP BY PHASE |  | DIST |  |  | Branch |  | LUM | WATT | AMP BY PHASE |  |  |  |  | DIST |  | Branch |  |
| # |  |  | L1 | L2 |  | feet |  |  |  | # |  | L1 |  | L2 |  |  |  | feet |  |  |
| LED SIGN | 20 |  | 0.2 |  |  | 500 | 1 |  |  | 18 | 250 |  |  | 2.8 |  |  |  | 190 | 1 |  |
| 1 | 250 |  |  | 2.8 |  | 240 | 1 |  |  | 19 | 250 | 2.8 |  |  |  |  |  | 110 | 1 |  |
| 2 | 250 |  | 2.8 |  |  | 240 | 1 |  |  | 20 | 70 |  |  | 0.7 |  |  |  | 30 | 1 |  |
| 3 | 250 |  |  | 2.8 |  | 190 | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4 | 250 |  | 2.8 |  |  | 190 | 1 |  |  | 21 | 70 | 0.7 |  |  |  |  |  | 35 | 2 |  |
| 5 | 250 |  |  | 2.8 |  | 230 | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6 | 250 |  | 2.8 |  |  | 190 | 1 |  |  | JB-F |  |  |  |  |  |  |  | 45 | 3 |  |
| 7 | 250 |  |  | 2.8 |  | 190 | 1 |  |  | 9 | 250 | 2.8 |  |  |  |  |  | 130 | 4 |  |
| 8 | 250 |  | 2.8 |  |  | 110 | 1 |  |  | 10 | 250 |  |  | 2.8 |  |  |  | 25 | 4 |  |
| JB A |  |  |  |  |  | 15 |  |  |  | 11 | 70 | 0.7 |  |  |  |  |  | 75 | 4 |  |
| CC |  |  |  |  |  |  |  |  |  | 12 | 70 |  |  | 0.7 |  |  |  | 50 | 4 |  |
| CIRCUITS 2 & 4 |  |  | L1 | L2 |  |  |  |  |  | 13 | 70 | 0.7 |  |  |  |  |  | 10 | 4 |  |
| TOTAL AMPS |  |  | 11.4 | 11.2 |  |  |  |  |  | JB-E |  |  |  |  |  |  |  | 60 | 5 |  |
| % IMBALANCE |  |  | 0.88% |  |  |  |  |  |  | 14 | 70 |  |  | 0.7 |  |  |  | 75 | 5 |  |
|  |  |  |  |  |  |  |  |  |  | 15 | 70 | 0.7 |  |  |  |  |  | 30 | 5 |  |
| Circuits 6, 8 (Exit Ramp) |  |  |  |  |  |  |  |  |  | 16 | 250 |  |  | 2.8 |  |  |  | 130 | 5 |  |
| LUM |  | WATT | AMP BY PHASE |  |  | DIST | Branch |  |  | 17 | 250 | 2.8 |  |  |  |  |  | 35 | 5 |  |
| 33 |  | 250 | 2.8 |  |  | 240 | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 32 |  | 250 |  | 2.8 |  | 240 | 1 |  |  | 22 | 250 |  |  | 2.8 |  |  |  | 200 | 6 |  |
| 31 |  | 250 | 2.8 |  |  | 240 | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 30 |  | 250 |  | 2.8 |  | 240 | 1 |  |  | 23 | 250 | 2.8 |  |  |  |  |  | 70 | 6 |  |
| 29 |  | 250 | 2.8 |  |  | 240 | 1 |  |  | JB-D |  |  |  |  |  |  |  | 115 | 6 |  |
| 28 |  | 250 |  | 2.8 |  | 210 | 1 |  |  | 24 | 250 |  |  | 2.8 |  |  |  | 80 | 6 |  |
| 27 |  | 250 | 2.8 |  |  | 220 | 1 |  |  | 25 | 70 | 0.7 |  |  |  |  |  | 80 | 6 |  |
| 26 |  | 250 |  | 2.8 |  | 55 | 1 |  |  | JB-C |  |  |  |  |  |  |  | 40 | 7 |  |
| JB-B |  |  |  |  |  | 100 | 1 |  |  | JB-B |  |  |  |  |  |  |  | 100 | 7 |  |
| JB-A |  |  |  |  |  | 15 | 1 |  |  | JB-A |  |  |  |  |  |  |  | 15 | 7 |  |
| CC |  |  |  |  |  |  | 1 |  |  | CC |  |  |  |  |  |  |  |  |  |  |
| CIRCUITS 4 & 6 |  |  | L1 | L2 |  |  |  |  |  | CIRCUITS 3 & 5 |  | L1 |  | L2 |  |  |  |  |  |  |
| TOTAL AMPS |  |  | 11.2 | 11.2 |  |  |  |  |  | TOTAL AMPS |  | 14.7 |  | 16.1 |  |  |  |  |  |  |
| % IMBALANCE |  |  | 0.00% |  |  |  |  |  |  | % IMBALANCE |  | 4.55% |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | CONTROL CENTER |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | L1* | L2 |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | OVERALL TOTAL |  | 39.0 | 38.5 |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | % IMBALANCE |  | 0.65% |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | * PHASE L1 HAS 1.7 AMPS ADDED TO ACCOUNT FOR THE PHOTOCELL |  |  |  |  |  |  |  |  |  |  |

| Table 2: Wire Size Program |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Car Parking & Ped. Lighting |  |  |  |  |  | Car Parking & Ped. Lighting |  |  |  |  |
| Number of Branches |  |  |  |  | 7 | Number of Branches |  |  |  | 7 |
| Line voltage |  |  |  |  | 120 VAC | Line voltage |  |  |  | 120 VAC |
| Maximum allowable voltage drop |  |  |  |  | 3% | Maximum allowable voltage drop |  |  |  | 3% |
| Circuit L1-5 |  |  | Branch #1 | Load (Amps) | Distance | Circuit L2-3 |  | Branch #1 | Load (Amps) | Distance |
|  | 1 |  | LUM. 19 | 2.8 | 140 |  | 1 | LUM. 18 | 2.8 | 300 |
|  |  |  |  |  |  |  | 2 | LUM.20 | 0.7 | 30 |
|  |  |  | Branch #2 | Load (Amps) | Distance |  |  |  |  |  |
|  | 1 |  | LUM. 21 | 0.7 | 35 |  |  | Branch #2 | Load (Amps) | Distance |
|  |  |  |  |  |  |  | 1 | JB-F | 0 | 0 |
|  |  |  | Branch #3 | Load (Amps) | Distance |  |  |  |  |  |
|  | 1 | JB-F |  | 3.5 | 45 |  |  | Branch #3 | Load (Amps) | Distance |
|  |  |  |  |  |  |  | 1 | JB-F | 3.5 | 45 |
|  |  |  | Branch #4 | Load (Amps) | Distance |  |  |  |  |  |
|  | 1 |  | LUM. 9 | 2.8 | 155 |  |  | Branch #4 | Load (Amps) | Distance |
|  | 2 |  | LUM. 11 | 0.7 | 125 |  | 1 | LUM. 10 | 2.8 | 100 |
|  | 3 |  | LUM. 13 | 0.7 | 10 |  | 2 | LUM. 12 | 0.7 | 60 |
|  |  |  | Branch #5 | Load (Amps) | Distance |  |  | Branch #5 | Load (Amps) | Distance |
|  | 1 | JB-E |  | 7.7 | 135 |  | 1 | JB-E | 7.0 | 60 |
|  | 2 |  | LUM. 15 | 0.7 | 160 |  | 2 | LUM. 14 | 0.7 | 105 |
|  | 3 |  | LUM. 17 | 2.8 | 35 |  | 3 | LUM. 16 | 2.8 | 165 |
|  |  |  | Branch #6 | Load (Amps) | Distance |  |  | Branch #6 | Load (Amps) | Distance |
|  | 1 |  | LUM. 23 | 2.8 | 265 |  | 1 | LUM. 22 | 2.8 | 315 |
|  | 2 |  | LUM. 25 | 0.7 | 80 |  | 2 | LUM. 24 | 2.8 | 160 |
|  |  |  | Branch #7 | Load (Amps) | Distance |  |  | Branch #7 | Load (Amps) | Distance |
|  | 1 |  | JB-C | 14.7 | 155 |  | 1 | JB-C | 16.1 | 155 |
|  | Required wire size: |  |  | #4 AWG |  |  | Required wire size: |  | #4 AWG |  |
| Truck Parking & Ent. Ramp |  |  |  |  |  | Exit Ramp |  |  |  |  |
| Circuit L1-2 |  |  | Branch #1 | Load (Amps) | Distance | Circuit L1-6 |  | Branch #1 | Load (Amps) | Distance |
|  | 1 |  | LED Sign | 0.2 | 740 |  | 1 | LUM. 33 | 2.8 | 480 |
|  | 2 |  | LUM. 2 | 2.8 | 430 |  | 2 | LUM. 31 | 2.8 | 480 |
|  | 3 |  | LUM. 4 | 2.8 | 460 |  | 3 | LUM. 29 | 2.8 | 450 |
|  | 4 |  | LUM. 6 | 2.8 | 380 |  | 4 | LUM. 27 | 2.8 | 390 |
|  | 5 |  | LUM. 8 | 2.8 | 125 |  |  |  |  |  |
|  | Required wire size: |  |  | #2 AWG |  |  | Required wire size: |  | #0 AWG |  |
| Circuit L2-4 |  |  | Branch #1 | Load (Amps) | Distance | Circuit L1-8 |  | Branch #1 | Load (Amps) | Distance |
|  | 1 |  | LUM. 1 | 0.2 | 480 |  | 1 | LUM. 32 | 2.8 | 480 |
|  | 2 |  | LUM. 3 | 2.8 | 420 |  | 2 | LUM. 30 | 2.8 | 480 |
|  | 3 |  | LUM. 5 | 2.8 | 420 |  | 3 | LUM. 28 | 2.8 | 430 |
|  | 4 |  | LUM. 7 | 2.8 | 315 |  | 4 | LUM. 26 | 2.8 | 170 |
|  | Required wire size: |  |  | #2 AWG |  |  | Required wire size: |  | #0 AWG |  |